## Heat Loss
www.hcheattransfer.com
1-877-542-1214
Ambient Heat Loss from a Vessel
This tool calculates the ambient heat losses from a vertical vessel.
Vessel Dimensions
| Tank diameter | (ft) | 50
| Vessel height | (ft) | 48
| Liquid height | (ft) | 30
| Sidewall insulation thickness | (inches) | 1.5
| Roof insulation thickness | (inches) | 0
Ambient Conditions
| Ambient temperature | (°F) | 35
| Wind speed | (mph) | 10
Liquid Properties
| Temperature | (°F) | 55
| Liquid specific heat | (BTU/lb/°F) | 0.6
| Liquid viscosity | (Centipoise) | 40
| Liquid thermal conductivity | (BTU/hr/ft/°F) | 0.12
| Liquid density | (lb/ft3) | 46.8
| Liquid coeff of thermal expansion | (/°F) | 1e-06
Vapor Properties
| Vapor specific heat | (BTU/lb/°F) | 0.25
| Vapor viscosity | (Centipoise) | 0.0175
| Vapor thermal conductivity | (BTU/hr/ft/°F) | 0.015
| Vapor density | (lb/ft3) | 0.08
| Vapour coeff of thermal expansion | (/°F) | 0.002
RESULTS
|  | Area | Heat Loss
| Location | (ft2) | (BTU/hr)
| Dry Wall | 2827.4334 | 6319.8297
| Wet wall | 4712.389 | 18129.7718
| Roof | 1967.3266 | 2717.0804
| Bottom | 1963.4954 | 1156.8334
| Total | 11470.6444 | 28323.5153
Yellow fields are input
Red fields are results
* These calculations are provided for educational use only - USE AT YOUR OWN RISK.
Assumptions
1. Roof slope = 0.75 inch/ft
2. Thickness of metal sidewalls and roof = 0.1875 inches
3. Thermal conductivity of metal sidewalls and roof = 26 BTU/Hr-ft-°F
4. Insulation Type = cellular glass
5. External surface has white paint with emmissivity = 0.9
6. Dirt factor for dry sidewall = 0.001 ft2.hr.°F/BTU
7. Dirt factor for wet sidewall = 0.00125 ft2.hr.°F/BTU
8. Dirt factor for bottom = 0.002 ft2.hr.°F/BTU
9. Dirt factor for bottom = 0.002 ft2.hr.°F/BTU
10. Dirt factor for roof = 0.001 ft2.hr.°F/BTU
11. Atmospheric pressure = 14.7 psia
12. Ground Temperature = 5°F above ambient temperature
13. Thermal Conductivity of ground = 0.8 BTU/Hr/ft/°F
14. Specific heat of air = 0.25 BTU/lb/°F
15. Viscosity of air = 0.0175 Centipoise
16. Thermal conductivity of air = 0.0151 BTU/Hr/ft/°F
17. Density of air = 0.0798 lb/ft3
18. Volumetric coeff of thermal expansion of air = 0.002 /°F
19. Temperature of vapor space = 5 °F cooler than liquid temperature
Calculations are based on:
Predict Storage Tank Heat Transfer Precisely by J.D. Kumana & S.P. Kothari, Chemical Engineering, March 22, 1982, P-127
Calculate the
h of liquid film on the wet wall surface |  |  |  | 1.4152 | BTU/hr/sf/°F
Outside wallTemperature |  |  |  | 42.5 | °F
Therm Cond Of Sidewall Insuln |  |  |  | 0.031292 | BTU/Hr/ft/°F
Therm Cond Of Roof Insuln |  |  |  | 0.031292 | BTU/Hr/ft/°F