## Calculations
www.hcheattransfer.com
1-877-542-1214
Preliminary Heat Exchanger Sizing
| This tool calculates the preliminary heat transfer area and utility requirements for shell and tube heat exchangers. |  |  |  |  | heating - vapour | Water | 0.75
[6 empty] | heating - liquid | Glycol | 1
| Process Side |  |  | E-101 |  | cooling - vapour | Refrigerant | 1.25
|  | Process Description (choose from list) |  | boiling |  | cooling - liquid | Steam
| Tin | Process Inlet Temperature | (oF) | 110 |  | condensing | Hot Oil
| Tout | Process Outlet Temperature | (oF) | 125 |  | boiling | Other
| Q | Duty | (BTU/hr) | 4000000
Utility Side
|  | Type of Fluid (choose from list) |  | Steam
| tin | Utility Inlet Temperature | (oF) | 400
| tout | Utility Outlet Temperature | (oF) | 398
| do | Tube Outside Diameter (choose from list) | (inches) | 1
| L | Tube Length | (ft) | 16
RESULTS
| DTlmtd | Log Mean temperature Difference | (oF) | 281.45
| U | Overall Heat Transfer coefficient | (Btu/hr-ft2-°F) | 120
| A | PRELIMINARY Heat Transfer Area | (ft2) | 118.4343
|  | Number of tubes |  | 28.2741
| D | Shell diameter (ID) | (in) | 10.02
|  | Utility Flow Rate | (lb/hr) | 4501.463
Yellow fields are input
Red fields are results
* These calculations are provided for educational use only - USE AT YOUR OWN RISK.
Assumptions
1. 1 tube pass countercurrent flow arrangement
2. 1.25 triangular pitch layout
3. Glycol properties are based on 50% (wt) Ethylene Glycol at 0 oC
4. Refrigerant properties based on R-134a at -10oC
5. Steam properties based on steam at 100 psia
6. Hot oil properties based on Dowtherm Q at 200 C

## TABLE
ACTUAL TUBE/SHELL TABLE |  |  |  | LOOKUP TUBE/SHELL TABLE
[5 empty] | Shell ID |  | Shell ID |  | Shell ID
Shell ID | 3/4" tubes | 1" tubes | 1 1/4" tubes | 3/4" tubes | 5.047 | 1" tubes | 5.047 | 1 1/4" tubes | 5.047
5.047 | 19 | 8 | 4 | 19 | 6.065 | 8 | 6.065 | 4 | 6.065
6.065 | 25 | 14 | 6 | 25 | 7.981 | 14 | 7.981 | 6 | 7.981
7.981 | 52 | 26 | 12 | 52 | 10.02 | 26 | 10.02 | 12 | 10.02
10.02 | 85 | 42 | 21 | 85 | 12 | 42 | 12 | 21 | 12
12 | 126 | 64 | 37 | 126 | 13.25 | 64 | 13.25 | 37 | 13.25
13.25 | 147 | 85 | 45 | 147 | 15.25 | 85 | 15.25 | 45 | 15.25
15.25 | 206 | 110 | 61 | 206 | 17.25 | 110 | 17.25 | 61 | 17.25
17.25 | 268 | 147 | 80 | 268 | 19.25 | 147 | 19.25 | 80 | 19.25
19.25 | 335 | 184 | 97 | 335 | 21.25 | 184 | 21.25 | 97 | 21.25
21.25 | 416 | 227 | 124 | 416 | 23.25 | 227 | 23.25 | 124 | 23.25
23.25 | 499 | 280 | 145 | 499 | 25 | 280 | 25 | 145 | 25
25 | 576 | 316 | 172 | 576 | 27 | 316 | 27 | 172 | 27
27 | 675 | 371 | 210 | 675 | 29 | 371 | 29 | 210 | 29
29 | 790 | 434 | 241 | 790 | 31 | 434 | 31 | 241 | 31
31 | 896 | 503 | 272 | 896 | 33 | 503 | 33 | 272 | 33
33 | 1018 | 576 | 310 | 1018 | 35 | 576 | 35 | 310 | 35
35 | 1166 | 643 | 356 | 1166 | 37 | 643 | 37 | 356 | 37
37 | 1307 | 738 | 396 | 1307 | 39 | 738 | 39 | 396 | 39
39 | 1464 | 804 | 442 | 1464 | 42 | 804 | 42 | 442 | 42
42 | 1688 | 946 | 518 | 1688 | 45 | 946 | 45 | 518 | 45
45 | 1943 | 1087 | 602 | 1943 | 48 | 1087 | 48 | 602 | 48
48 | 2229 | 1240 | 682 | 2229 | 51 | 1240 | 51 | 682 | 51
51 | 2513 | 1397 | 770 | 2513 | 54 | 1397 | 54 | 770 | 54
54 | 2823 | 1592 | 862 | 2823 | 60 | 1592 | 60 | 862 | 60
60 | 3527 | 1969 | 1084 | 3527 |  | 1969 |  | 1084
Note on A4: H&C: Shell ID offset by 1 to return shell size 1 incrment up rather than down
Note on G3: H&C: Shell ID offset by 1 to return shell size 1 incrment up rather than down
Note on I3: H&C: Shell ID offset by 1 to return shell size 1 incrment up rather than down
Note on K3: H&C: Shell ID offset by 1 to return shell size 1 incrment up rather than down